Communication & Network Engineering

Applied Project  																																																																																																																																																																				       	DR / AMIR ELSAFRAWY

PRESENTED BY :

-Ahmed Nabil Abd El Hamed Siam.

-Oday Haitham Metwalli Hussein.

-Mohamed Ahmed Awad El Awaad.

-Abstract:

This project presents the design, implementation, and testing of a low-cost cooling controller system that maintains environmental temperature within a safe range using two 12V fans controlled by an ESP32 microcontroller. The system employs a DS18B20 digital temperature sensor for accurate readings and operates based on three predefined temperature thresholds (30°C, 40°C, and 55°C). At the highest threshold, it triggers an alert via the Blynk IoT mobile app and sends an email notification to a Gmail account. The design incorporates a 12V-to-5V regulator for power management and an NPN transistor-based level-shifter to interface the ESP32's 3.3V logic with 5V components. The prototype was constructed, tested on hardware, and validated through simulation, demonstrating reliable performance in maintaining temperature control while providing remote monitoring capabilities.

-Introduction:

In various applications such as server rooms, greenhouses, or industrial enclosures, maintaining optimal temperature is crucial to prevent equipment damage, ensure safety, and optimize performance. Traditional cooling systems can be expensive and energy-intensive. This project addresses the need for a cost-effective, IoT-enabled solution by developing a simple cooling controller using off-the-shelf components.

The system leverages the ESP32 microcontroller for its Wi-Fi capabilities, enabling remote monitoring and alerts. Two 12V fans are activated based on temperature thresholds to provide scalable cooling. The DS18B20 sensor offers precise digital temperature measurement, while the Blynk app and Gmail integration allow for real-time notifications. The inclusion of a voltage regulator and level-shifter ensures compatibility between components operating at different voltages.

This report outlines the project's objectives, design methodology, implementation details, testing results, and conclusions, providing a comprehensive overview suitable for academic or professional discussion.

-Objectives:

The primary objectives of this project are:

To design a low-cost cooling controller that maintains temperature within a safe range (below 55°C) using automated fan control.

To integrate IoT functionality for remote monitoring and alerting via the Blynk app and email.

To ensure hardware compatibility through appropriate voltage regulation and level-shifting.

To build, test, and simulate the system to verify its reliability and performance.

Methodology

1-System Design:

The cooling controller operates on a threshold-based logic:

1-Threshold 1 (30°C): Activate the first fan for mild cooling.

2-Threshold 2 (40°C): Activate both fans for increased cooling.

3-Threshold 3 (55°C): Maintain both fans active and trigger an alert via Blynk and Gmail.

The ESP32 reads temperature data from the DS18B20 sensor via a one-wire protocol. Fan control is achieved using PWM signals from the ESP32's GPIO pins, amplified through the NPN transistor level-shifter to drive the 12V fans.

2-Components Used:

1-ESP32 microcontroller (with Wi-Fi for IoT).

2-DS18B20 temperature sensor.

3-Two 12V DC fans.

4-12V-to-5V buck regulator (e.g., LM2596 module).

5-NPN transistor (e.g., 2N2222) for level-shifting.

5-Resistors, capacitors, and wiring for the circuit.

6-Blynk app for mobile interface.

7-SMTP server integration for Gmail notifications.

Circuit Design:

8-Power Supply: 12V input is regulated to 5V for the ESP32 and sensor.

9-Level-Shifter: Converts ESP32's 3.3V output to 5V for fan control (transistor acts as a switch).

10-Sensor Interface: DS18B20 connected to ESP32's GPIO with a 4.7kΩ pull-up resistor.

11-Fan Control: Transistor gates connected to ESP32 PWM pins, sourcing power from 12V supply.

12-A schematic diagram is provided in Appendix A.

3-Software Design:

The firmware was developed using the Arduino IDE with the ESP32 board package. Libraries used include:

1-OneWire and DallasTemperature for DS18B20.

Blynk for IoT app integration.

2-ESP32's WiFi and SMTP libraries for email.

The code implements a loop that:

-Reads temperature every 5 seconds.

-Compares against thresholds and controls fans accordingly.

-Sends alerts at 55°C.

-Sample code snippets are in Appendix B.

4-Simulation and Prototyping:

-Simulation: The circuit was modeled in Proteus or LTspice to verify voltage levels, current draw, and logic operations.

-Prototyping: Components were assembled on a breadboard, then soldered onto a PCB for durability.

5-Implementation:

-The prototype was built using the designed circuit. The ESP32 was programmed with the threshold logic, and Blynk was configured with virtual pins for temperature display and alerts. Gmail SMTP was set up using an app password for secure email sending.

-Hardware testing involved placing the system in a controlled environment (e.g., a heated enclosure) to observe fan activation and alert triggers. IoT functionality was verified by monitoring the Blynk app on a mobile device and checking email receipts.

6-Results and Testing:

-Hardware Testing

1-Temperature Accuracy: DS18B20 readings were calibrated against a reference thermometer, showing ±0.5°C accuracy.

2-Fan Operation: Fans activated correctly at thresholds (one at 30°C, both at 40°C, sustained at 55°C).

3-Voltage Levels: Regulator output stable at 5V; level-shifter ensured proper 5V signals for fans.

4-Power Consumption: System drew ~2A at full fan operation, efficient for low-cost applications.

7-Simulation Verification:

Simulations confirmed no voltage drops or logic errors.

PWM signals were validated for smooth fan speed control.

IoT Integration

Blynk app displayed real-time temperature and sent push notifications at 55°C.

Email alerts were received promptly via Gmail, with customizable messages.

The system successfully maintained temperatures below 55°C in tests, with alerts triggering reliably. No failures were observed in 10+ test cycles.

8) Safety & Reliability

•	Use a fuse on the 12 V fan supply (e.g., 1–2 A fast/medium‑blow).

•	Ensure proper wire gauge and tight connections to avoid heat.

•	Consider keeping fans ON at ≥55 °C while still alerting, depending on the application (e.g., cabinet fire policy vs. protect hardware). See Section 12 for configurable modes.

•	If fans draw large startup currents, enable a soft‑start (stagger Fan‑2 by 300–500 ms).

10) Possible Improvements (Practical & Useful)

•	PWM fan speed control using MOSFETs or 4‑wire PWM fans to vary speed smoothly (quieter, saves power).

•	PID or two‑point with hysteresis: hold a target temperature (e.g., 35 °C) and adjust duty cycle automatically.

•	Configurable threshold profiles from the Blynk app (edit 30/40/55 °C without reflashing).

•	Data logging: store temperature and fan states to microSD or Blynk cloud; show trends/graphs.

•	Multiple sensors & averaging: add extra DS18B20s at different locations; detect sensor fault (disconnected = 85 °C reading) and fail‑safe.

•	Enclosure & airflow design: ducts, dust filters, and mounting grill to improve cooling efficiency and safety.

•	Hardware drivers: replace relays with logic‑level N‑MOSFETs (with flyback diodes) for higher reliability and silent switching.

•	Power protection: TVS diode on 12 V line, reverse polarity diode, and over‑current protection.

•	OTA updates: enable OTA (Over‑the‑Air) firmware updates through Wi‑Fi.

•	Battery or solar option with power‑save modes; ESP32 deep sleep when stable.

•	Local UI: small OLED display and push‑buttons for manual mode and threshold setting.

•	Smart alarms: escalating alerts (app → email → buzzer) and auto‑retry logic; include GPS/time stamps in messages.

-Appendices:

Appendix A: Schematic Diagram

-Appendix B: Sample Code Snippet:

#define BLYNK_TEMPLATE_ID "TMPL2kNqU_oel"

#define BLYNK_TEMPLATE_NAME "ds18b20"

#define BLYNK_AUTH_TOKEN "04Mxd44COY9UhHAGFpOlqzkxTsNOK97x"

#include <WiFi.h>

#include <BlynkSimpleEsp32.h>

#include <OneWire.h>

#include <DallasTemperature.h>

// 📌 تعريفات الأجهزة والثوابت

#define ONE_WIRE_BUS 4

#define RELAY1 18 // مخرج الريلاي 1

#define RELAY2 19 // مخرج الريلاي 2

// 🌐 معلومات شبكة WiFi

char ssid[] = "FEE";

char pass[] = "2027##2727feee";

// ⏱️ متغيرات Blynk و Timer

BlynkTimer timer;

// 🌡️ تعريف كائنات الحساسات في النطاق العام (Global Scope)

OneWire oneWire(ONE_WIRE_BUS);

DallasTemperature sensors(&oneWire);

// ⚙️ حدود التشغيل والتحكم (الثوابت)

const float FAN1_ON = 30.0;

const float FAN2_ON = 40.0;

const float FIRE_ALARM = 55.0; // الحد الذي يشغل الإنذار والإشعار

// 💡 حالات الريلاي وعلم الإنذار (للتتبع وضمان إشعار واحد)

bool fan1State = false;

bool fan2State = false;

bool fireAlarm = false; // علم حالة الإنذار

// ---------------------------------------------

// 📤 دالة إرسال درجة الحرارة إلى Blynk والتحكم في الريلاي

void sendTemperature() {

// 1. القراءة من الحساس

sensors.requestTemperatures();

float tempC = sensors.getTempCByIndex(0);

float tempF = sensors.toFahrenheit(tempC);

// 2. إرسال القيم إلى Blynk (V0: Celsius, V1: Fahrenheit)

Blynk.virtualWrite(V0, tempC);

Blynk.virtualWrite(V1, tempF);

Serial.print("Blynk Temp C: ");

Serial.println(tempC);

// 3. منطق التحكم بالريلاي والإشعارات

// 🔥 حالة الحريق (الإنذار)

if (tempC >= FIRE_ALARM) {

if (!fireAlarm) {

// 🚨 إرسال الحدث إلى Blynk (يجب إعداده مسبقاً في Blynk Console)

Blynk.logEvent("fire_alert", String("⚠️ الحرارة تجاوزت الحد! القراءة: ") + tempC + " °C");

Serial.println("🚨🔥 إنذار حريق! تم إرسال إشعار Blynk 🔥🚨");

fireAlarm = true; // نضبط العلم لضمان الإرسال مرة واحدة

}

// إطفاء (أو تشغيل) جميع المراوح في حالة الإنذار (حسب منطقك السابق)

digitalWrite(RELAY1, LOW);

digitalWrite(RELAY2, LOW);

fan1State = false;

fan2State = false;

}

// 🔹 الحالة العادية (أقل من الإنذار)

else {

// 💡 إعادة تعيين حالة الإنذار (لتمكين إرسال تنبيه جديد لاحقاً)

if (fireAlarm) {

fireAlarm = false;

Serial.println("✅ تم إعادة تعيين نظام الإنذار.");

}

// التحكم في المروحة 1

if (tempC >= FAN1_ON && !fan1State) {

digitalWrite(RELAY1, HIGH); // تشغيل

fan1State = true;

Serial.println("✅ تشغيل المروحة 1");

} else if (tempC < FAN1_ON && fan1State) {

digitalWrite(RELAY1, LOW); // إيقاف

fan1State = false;

Serial.println("🟡 إيقاف المروحة 1");

}

// التحكم في المروحة 2

if (tempC >= FAN2_ON && !fan2State) {

digitalWrite(RELAY2, HIGH); // تشغيل

fan2State = true;

Serial.println("✅ تشغيل المروحة 2");

} else if (tempC < FAN2_ON && fan2State) {

digitalWrite(RELAY2, LOW); // إيقاف

fan2State = false;

Serial.println("🟡 إيقاف المروحة 2");

}

}

}

// ---------------------------------------------

void setup() {

// 🔴 الإعداد التسلسلي

Serial.begin(115200);

// 🌡️ إعداد الحساسات

sensors.begin();

// ⚡ إعداد الريلاي كمخارج

pinMode(RELAY1, OUTPUT);

pinMode(RELAY2, OUTPUT);

// الحالة الأولية للريلاي (إيقاف تشغيل)

digitalWrite(RELAY1, LOW);

digitalWrite(RELAY2, LOW);

// 🌐 إعداد Blynk والاتصال بالـ WiFi

Blynk.begin(BLYNK_AUTH_TOKEN, ssid, pass);

// ⏰ جدولة دالة إرسال الحرارة والتحكم كل 2000 ميللي ثانية (2 ثانية)

timer.setInterval(2000L, sendTemperature);

Serial.println("🔥 نظام Blynk ومراقبة الحرارة جاهز 🔥");

}

// ---------------------------------------------

void loop() {

// 🏃 تشغيل خدمات Blynk

Blynk.run();

// ⏰ تشغيل الـ Timer لجدولة الدالة

timer.run();

}

11-Conclusion:

-This project successfully demonstrates a low-cost, effective cooling controller with IoT capabilities. The use of ESP32, DS18B20, and threshold-based control provides a scalable solution for temperature management. Hardware compatibility was ensured through the regulator and level-shifter, and testing validated the system's reliability.

-Future enhancements could include additional sensors (e.g., humidity), cloud data logging, or integration with home automation systems. This project highlights the potential of IoT in simple embedded systems, making it suitable for educational or industrial applications.